## P1_Units
Unit Number | Unit Type | Unit Name | Unit Identifier | Q
1 | Source | source | Source
2 | Merge | E3_return | E3 Return
3 | Merge | E2_return | E2 Return
4 | Merge | E1_return | E1 Return
5 | Splitter | Supplemental_supply | Supplemental Converter Supply
6 | SimpleHeatExchanger | Suppl_Cond_Cooler | Supplemental Condensate Cooler | 80000
7 | Splitter | Cond_Splitter | Supplemental Condensate Cooler Splitter
8 | Merge | Cond_Merger | Supplemental Condensate Return Merger
9 | SimpleHeatExchanger | Supplemental_Converter | Supplemental Steam Converter | 1020000
10 | Merge | Supplemental_return | Supplemental Converter Return
11 | Splitter | Admin_total_supply | Admin Building Supply
12 | SimpleHeatExchanger | Admin_HEX | Admin Building HEX | -150000
13 | Merge | Admin_total_return | Admin Building Return
14 | Splitter | Control_Center_supply | Control Center supply
15 | SimpleHeatExchanger | Control_Center_HEX | Control Center HEX | -130000
16 | Merge | Control_Center_return | Control Center return
17 | Splitter | Digester_5_6_supply | Digester 5 6 supply
18 | SimpleHeatExchanger | Digester_5_6_HEX | Digester 5 6 HEX | -160000
19 | Merge | Digester_5_6_return | Digester 5 6 return
20 | Splitter | Boiler_A_supply | Boiler A supply
21 | SimpleHeatExchanger | Boiler_A_HEX | Boiler A HEX | -250000
22 | Merge | Boiler_A_return | Boiler A return
23 | Splitter | Boiler_B_supply | Boiler B supply
24 | SimpleHeatExchanger | Boiler_B_HEX | Boiler B HEX | -250000
25 | Merge | Boiler_B_return | Boiler B return
26 | Splitter | Digester_7_to_10_supply | Digester 7 to 10 supply
27 | SimpleHeatExchanger | Digester_7_to_10_HEX | Digester 7 to 10 HEX | -140000
28 | Merge | Digester_7_to_10_return | Digester 7 to 10 return
29 | Splitter | Digester_15_16_supply | Digester 15 16 supply
30 | SimpleHeatExchanger | Digester_15_16_HEX | Digester 15_ 16 HEX | -120000
31 | Splitter | Digester_11_to_14_supply | Digester 11 to 14 supply
32 | SimpleHeatExchanger | Digester_11_to_14_HEX | Digester 11 to 14 HEX | -150000
33 | Merge | Digester_11_to_14_return | Digester 11 to 14 return
34 | Merge | Digester_15_16_return | Digester 15 16 return
35 | Splitter | Waste_HEX1_supply | Waste HEX1 supply
36 | SimpleHeatExchanger | Waste_HEX1 | Waste HEX1 | -175000
37 | Merge | Waste_HEX2_return | Waste HEX2 return
38 | SimpleHeatExchanger | Waste_HEX2 | Waste HEX2 | -175000
39 | Splitter | Waste_HEX2_supply | Waste HEX2 supply
40 | Merge | Waste_HEX1_return | Waste HEX1 return
41 | Splitter | E1_supply | E1 supply
42 | SimpleHeatExchanger | JW_HEX_E1 | JW HEX E1 | 200000
43 | Splitter | E2_supply | E2 supply
44 | SimpleHeatExchanger | JW_HEX_E2 | JW HEX E2 | 200000
45 | Splitter | E3_supply | E3 supply
46 | SimpleHeatExchanger | JW_HEX_E3 | JW HEX E3 | 200000
47 | Sink | sink | Sink

## P1_Connections
Connection Number | Connection Type | Connection Name | Start Unit Name | Start Unit Port | End Unit Name | End Unit Port | Label | fluid | mass flow rate | temperature | pressure
1 | Connection | c1 | source | out1 | E3_return | in1 | 1 | water | 50 | 55 | 101.325
2 | Connection | c1a | JW_HEX_E3 | out1 | E3_return | in2 | 1a |  |  | 80
3 | Connection | c2a | JW_HEX_E2 | out1 | E2_return | in2 | 2a |  |  | 80
4 | Connection | c2 | E3_return | out1 | E2_return | in1 | 2
5 | Connection | c3 | E2_return | out1 | E1_return | in1 | 3
6 | Connection | c3a | JW_HEX_E1 | out1 | E1_return | in2 | 3a |  |  | 80
7 | Connection | c4 | E1_return | out1 | Supplemental_supply | in1 | 4
8 | Connection | c6 | Supplemental_supply | out1 | Supplemental_return | in1 | 6
9 | Connection | c6a | Supplemental_supply | out2 | Cond_Splitter | in1 | 6a
10 | Connection | c6b | Cond_Splitter | out1 | Cond_Merger | in1 | 6b
11 | Connection | c6c | Cond_Splitter | out2 | Suppl_Cond_Cooler | in1 | 6c |  | 25
12 | Connection | c6d | Suppl_Cond_Cooler | out1 | Cond_Merger | in2 | 6d
13 | Connection | c6e | Cond_Merger | out1 | Supplemental_Converter | in1 | 6e
14 | Connection | c6f | Supplemental_Converter | out1 | Supplemental_return | in2 | 6f |  |  | 92
15 | Connection | c7 | Supplemental_return | out1 | Admin_total_supply | in1 | 7
16 | Connection | c7a | Admin_total_supply | out2 | Admin_HEX | in1 | 7a |  | 20
17 | Connection | c8 | Admin_total_supply | out1 | Admin_total_return | in1 | 8
18 | Connection | c8a | Admin_HEX | out1 | Admin_total_return | in2 | 8a
19 | Connection | c9 | Admin_total_return | out1 | Control_Center_supply | in1 | 9
20 | Connection | c9a | Control_Center_supply | out2 | Control_Center_HEX | in1 | 9a |  | 25
21 | Connection | c10 | Control_Center_supply | out1 | Control_Center_return | in1 | 10
22 | Connection | c10a | Control_Center_HEX | out1 | Control_Center_return | in2 | 10a
23 | Connection | c11 | Control_Center_return | out1 | Digester_5_6_supply | in1 | 11
24 | Connection | c11a | Digester_5_6_supply | out2 | Digester_5_6_HEX | in1 | 11a |  | 22
25 | Connection | c12 | Digester_5_6_supply | out1 | Digester_5_6_return | in1 | 12
26 | Connection | c12a | Digester_5_6_HEX | out1 | Digester_5_6_return | in2 | 12a
27 | Connection | c13 | Digester_5_6_return | out1 | Boiler_A_supply | in1 | 13
28 | Connection | c13a | Boiler_A_supply | out2 | Boiler_A_HEX | in1 | 13a |  | 25
29 | Connection | c14 | Boiler_A_supply | out1 | Boiler_A_return | in1 | 14
30 | Connection | c14a | Boiler_A_HEX | out1 | Boiler_A_return | in2 | 14a
31 | Connection | c15 | Boiler_A_return | out1 | Boiler_B_supply | in1 | 15
32 | Connection | c15a | Boiler_B_supply | out2 | Boiler_B_HEX | in1 | 15a |  | 20
33 | Connection | c16 | Boiler_B_supply | out1 | Boiler_B_return | in1 | 16
34 | Connection | c16a | Boiler_B_HEX | out1 | Boiler_B_return | in2 | 16a
35 | Connection | c17 | Boiler_B_return | out1 | Digester_7_to_10_supply | in1 | 17
36 | Connection | c17a | Digester_7_to_10_supply | out2 | Digester_7_to_10_HEX | in1 | 17a |  | 25
37 | Connection | c18 | Digester_7_to_10_supply | out1 | Digester_7_to_10_return | in1 | 18
38 | Connection | c18a | Digester_7_to_10_HEX | out1 | Digester_7_to_10_return | in2 | 18a
39 | Connection | c19 | Digester_7_to_10_return | out1 | Digester_15_16_supply | in1 | 19
40 | Connection | c19a | Digester_15_16_supply | out2 | Digester_15_16_HEX | in1 | 19a |  | 10
41 | Connection | c20 | Digester_15_16_supply | out1 | Digester_11_to_14_supply | in1 | 20
42 | Connection | c20a | Digester_11_to_14_supply | out2 | Digester_11_to_14_HEX | in1 | 20a |  | 20
43 | Connection | c21 | Digester_11_to_14_supply | out1 | Digester_11_to_14_return | in1 | 21
44 | Connection | c21a | Digester_11_to_14_HEX | out1 | Digester_11_to_14_return | in2 | 21a
45 | Connection | c22 | Digester_11_to_14_return | out1 | Digester_15_16_return | in1 | 22
46 | Connection | c23 | Digester_15_16_HEX | out1 | Digester_15_16_return | in2 | 23
47 | Connection | c24 | Digester_15_16_return | out1 | Waste_HEX1_supply | in1 | 24
48 | Connection | c24a | Waste_HEX1_supply | out2 | Waste_HEX1 | in1 | 24a |  | 25
49 | Connection | c25 | Waste_HEX1_supply | out1 | Waste_HEX2_return | in1 | 25
50 | Connection | c26 | Waste_HEX2_return | out1 | Waste_HEX2_supply | in1 | 26
51 | Connection | c27 | Waste_HEX2_supply | out1 | Waste_HEX1_return | in1 | 27
52 | Connection | c27a | Waste_HEX1 | out1 | Waste_HEX1_return | in2 | 27a
53 | Connection | c26a | Waste_HEX2_supply | out2 | Waste_HEX2 | in1 | 26a |  | 25
54 | Connection | c25a | Waste_HEX2 | out1 | Waste_HEX2_return | in2 | 25a
55 | Connection | c28 | Waste_HEX1_return | out1 | E1_supply | in1 | 28
56 | Connection | c28a | E1_supply | out2 | JW_HEX_E1 | in1 | 28a
57 | Connection | c29 | E1_supply | out1 | E2_supply | in1 | 29
58 | Connection | c29a | E2_supply | out2 | JW_HEX_E2 | in1 | 29a
59 | Connection | c30 | E2_supply | out1 | E3_supply | in1 | 30
60 | Connection | c30a | E3_supply | out2 | JW_HEX_E3 | in1 | 30a
61 | Connection | c31 | E3_supply | out1 | sink | in1 | 31